SYSTEM SENSOR RRS MODULE WIRING DIAGRAM

VISTA 20 P PANEL - SYSTEM SENSOR 2WTAB SMOKE DETECTORS.

RRS MODULE USED TO ENERGIZE SMOKE DETECTOR TONERS
RRS MODULE WIRING

RRS DIP SWITCH MUST BE  SET TO OFF 

BLACK-
V 20P TERMINAL  # 4 ( AUX - )

RED-

V 20P TERMINAL  # 5  ( AUX +)  

PURPLE-
FROM  RRS MODULE  CONNECTS TO V 20P  TERMINAL # 3 



BELL OUTPUT + ( PULSING )

YELLOW-
FROM RRS MODULE CONNECTS TO V 20P TERMINAL # 8 (ZN1 HI)

ORANGE-
FROM RRS MODULE CONNECTS TO V 20P TERMINAL # 9 (ZN1  LO)

BROWN-
FROM RRS MODULE TO POSITIVE (+) FEED WIRE OF SMOKE 



DETECTORS IN FIELD

WHITE-
FROM RRS MODULE TO NEGATIVE (-) FEED WIRE OF SMOKE



DETECTORS IN FIELD

NOTES

FROM THE WHITE WIRE OF THE RRS MODULE TO THE ORANGE WIRE OF THE RRS MODULE (WHICH IS CONNECTED TO V20P TERMINAL 9  YOU NEED TO INSTAL A  470   OHM RESISTOR  < IF YOU DO NOT HAVE A 470  OHM RESISTOR – YOU CAN PARALLEL  2 - 1,000 OHM RESISTORS )

ZONE # 1 (V 20P TERMINALS 8 & 9 ) IS A DEDICATED 2 WIRE SMOKE DETECTOR ZONE. 2 WIRE SMOKE DETECTORS MUST BE WIRED TO ZONE # 1

YOU MAY ONLY INSTAL 2 WIRE DEVICES ON ZONE 1 (2 WIRE SMOKES OR HEAT DETECTORS )

ALL FIRE DEVICES CONNECTED TO ANY OTHER ZONE WILL CAUSE THE 2WTAB SMOKE DETECTOR TONERS TO ACTIVATE
