SYSTEM SENSOR RRS MODULE WIRING DIAGRAM

VISTA 20 P PANEL - SYSTEM SENSOR 4WTAB SMOKE DETECTORS.

RRS MODULE USED TO ENERGIZE SMOKE DETECTOR TONERS

VISTA 20P NOTES

DO NOT PUT 4 WIRE SMOKE DETECTORS ON ZONE 1 OF THE VISTA 20P

THIS IS A DEDICATED 2 WIRE SMOKE ZONE.

YOU CAN UTILIZE MORE THAN 1 ZONE FOR FIRE – THE RRS MODULES WILL STILL SOUND THE TONERS REGARDLESS OF WHAT FIRE ZONE WENT OFF.

RRS MODULE WIRES

RRS DIP SWITCH MUST BE  SET TO OFF 

PURPLE

WIRE TO VISTA 20P – TERMINAL 3  ( BELL + ) 

RED & YELLOW:
2 OPTIONS (Depends on location of the 4229 module)





A: Wire  RED & YELLOW DIRECT TO VISTA 20P





      TERMINAL   5  (AUX + )








OR




     
B:  Wire RED & YELLOW DIRECT TO 4229  





       TERMINAL  3 (AUX + )

ORANGE & BLACK:
     WIRE TO 4229 RELAY MODULE – RELAY 1 





     ORANGE            (N.C.) WIRE.

BROWN WIRE: 
WIRE TO POSITIVE     (+) OF FIELD SMOKE DET’S.

WHITE   WIRE:
            WIRE TO NEGATIVE   ( - )  OF FIELD SMOKE DET’S.

SYSTEM SENSOR RRS MODULE WIRING DIAGRAM

VISTA 20 P PANEL - SYSTEM SENSOR 4WTAB SMOKE DETECTORS.

4229 WIRING

SET ADDRESS DIP SWITCH FOR CORRECT ADDRESS

PUT TAMPER JUMPER INTO THE UPPER (NOT TAMPERED) POSITION

WIRE THE 4229 TO THE VISTA 20P AS YOU NORMALLY WOULD

4229 TERMINAL TB 2 #      VISTA 20P TERMINAL #            22/4 COLOR 



1


7  (DATA IN)


WHITE



2


5  (  + 12 V )


RED


3


4  (   - 12 V )


BLACK



4


6   (DATA OUT)

GREEN
4229  PROGRAMMING  CONFIGURES THE LOWER RELAY (# 1) FOR THE SMOKE RESET FUNCTION

THE RELAY CONNECTOR WIRING HARNESS HAS 7 WIRES.

YOU WILL ONLY NEED THE   ORANGE (N.C.)  & BROWN (N.O.) WIRES.

ORANGE (N.C.) WIRE  - WIRED TO THE ORANGE & BLACK RRS MODULE WIRES.

BROWN WIRE – CONNECT TO THE 4229 TERMINAL  # 3  ( - )

