VISTA 128FBP

USING 4209 U MODULES AND MULTIPLE RS-MODS AND 2 WIRE SMOKE DETECTORS WITH TONERS

(DARELENE JORDAN – 77207-4092 – ACCOUNT NAME IN COMPASS)

PROGRAM WITH SERIAL NUMBERS 

1- WIRING NOTES

a- Ok to use Honeywell Step by Step 

i. – if more than 3 zones of 2 wire protection:

1. OK to use loop C of 4209U. 
BUT – YOU MUST 

NOT use loop D. (leave w/resistor) and do not 

Program the serial # in the panel

b- Do not use Zone 9 as the first zone of a module Start  @ 12.

c- Install 1 4204 Relay Board for Each 4209U used.

d- (Jordan’s – needed additional power supply)

e- Check dip-switches.

f- Make sure power to reset smokes is applied to the NC contact of RELAY 4 of Each 4204 BOARD. (Wire to Terminal 11 of the 128 FBP)

g- Make sure that there is a wire from the C of the @ 4 Relay of Each Board used to the 4209U Module it is associated with.

2- PROGRAMMING NOTES:

1- PROGRAM the 4209U’s in serial Mode programming again start as zone 

12.       ZONE MENU PROGRAMMING

· RESPONSE = 9

· PART
=
1

· Input Type=
6

· Loop #

1

· Serial #
000000

· Bell

1

2- DEVICE MENU PROGRAMMING

· 4204 modules

i. - # 1 = Address 8  (DEVICE TYPE = 4)

ii. - # 2 = Address 9  (DEVICE TYPE = 4)

3- GLOBALS:

· SYSTEM OPTIONS – TO ADD TO NORMAL PROGRAMMING



i. AUTO TROUBLE RESTORE

FIRE OPTIONS:


Do NOT check RESET BELLS after 2nd Off Function

4- RELAY: 

· OUTPUT DEVICES

· Output # 1

description (associated zone #)

Device # 1


      Group #

0

Action=
2 (Close and stay closed)


       Restrict


Add’l Bell

Start Zone# =
0

Start Parameters




Stop Parameters


Event
=
1-  Alarm





Zone List=
1



Zone List = 0


Type=

0 (No response)

Type=
  22 (Disarm Code + off )


Partition=
1 – P1



Partition=
1

Access / relay trigger parameters



Relay Type=

1   4204 Relays

ECP address = 8










Relay =
1

This follows the same for relays 1 - 3 on each module used.

· Zone list  - determined by the zone activated. Each zones list corresponds to the other zones in the system (even regular zones – ie not on 4209U)

example
( Jordans residence )



Output 1 
=
zone 17



List 1

=
you would check off






3-13-14-15-18-19



output 2
=
zone 18



List 2

=
3-13-14-15-17-19



Etc

RELAY 4 IS DIFFERENT AND MUST BE PROGRAMMED THIS WAY WHEN

USING LISTS: (Using Jordans as an example)


Output # 1


DESCRIPTION
smoke reset
      Group #

0

Action=
1 (Close for 2 seconds)


       Restrict


Add’l Bell

Start Zone# =
0

Start Parameters




Stop Parameters


Event
=
0-  Not used





Zone List=
0



Zone List = 0


Type=

54 (Smoke Det Reset)

Type=
  0 (No response)


Partition=
1 – P1



Partition=
0 (Any partition)

Access / relay trigger parameters



Relay Type=

1   4204 Relays

ECP address = 8










Relay =
4

